BlueSim Training Guide

Auto Load Sharing & Preferential Trip

Electrical & Power

Automatic load sharing between parallel generators with isochronous/droop mode selector and preferential trip system for non-essential loads.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Automatic load sharing between parallel generators with isochronous/droop mode selector and preferential trip system for non-essential loads.

## Key Features

Isochronous and droop mode load sharing with live kW/kVAr meters.

Load sharing error display and imbalance detection.

Preferential trip panel with 80/90/95% bus load setpoints.

Live load curve trend chart showing 60-second history.

Four scenarios: Overload Trip Sequence, Manual Restoration, Load Imbalance, DG2 Trip.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| GENERATOR METERS | Displays real-time system data, controls, and status indicators. |
| BUS DIAGRAM & LOAD TREND | Displays real-time system data, controls, and status indicators. |
| ALARMS & SETPOINTS | Displays real-time system data, controls, and status indicators. |
| BUS SUMMARY | Displays real-time system data, controls, and status indicators. |
| PREFERENTIAL TRIP PANEL | Displays real-time system data, controls, and status indicators. |
| SCENARIO | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Auto Load Sharing & Preferential Trip — Technical Reference

### Overview

When two or more generators operate in parallel on the same busbar, a load sharing system ensures each machine carries a proportional share of the total load. If total demand exceeds generator capacity, a preferential trip system automatically disconnects non-essential loads to protect the generators.

### Regulatory Basis

**SOLAS II-1/Reg.41** — Main and emergency sources of electrical power

**IEC 60092-301** — Marine generators in parallel operation

**IEC 60092-302** — Switchboards — protection requirements

**Classification Rules** (DNV, LR, ABS) — Preferential trip setpoints

### Load Sharing Methods

#### Isochronous (Equal Frequency) Mode

Both generators maintain exactly 60.0 Hz regardless of load

Load is shared equally (or as per setpoint) via load sharing relay

Requires interconnection between governor controllers

Result: Very stable frequency, exact proportional sharing

#### Droop Mode

Each generator has a frequency droop characteristic (typically 3–5%)

As load increases, frequency drops slightly — this naturally "tilts" load between machines

At 0% load: machine runs at 100% rated speed

At 100% load: machine drops to ~95–97% speed

Result: Inherent load sharing without interconnect, but frequency varies

#### Load Sharing Error

**Positive error (>±5%):** One machine taking more than its share

**Negative error (>±5%):** One machine running light

Causes: Governor droop mismatch, fuel rack sticking, sensor fault

Correction: Adjust isochronous set-point or governor droop setting

### kW / kVAr Sharing

#### kW (Active Power) Sharing

Controlled by governor speed/fuel setting:

Increase fuel → generator frequency rises → it takes more kW

Decrease fuel → generator frequency drops → it sheds kW

#### kVAr (Reactive Power) Sharing

Controlled by AVR voltage setting:

Increase AVR voltage → generator exports reactive power (lagging)

Decrease AVR voltage → generator absorbs reactive power (leading)

Mismatched kVAr sharing → circulating reactive currents → heating

### Preferential Trip System

#### Purpose

Protect the running generators from overload by automatically disconnecting non-essential loads in a pre-defined sequence.

#### Trip Sequence (Typical)

| Level | Bus Load | Action |

|-------|----------|--------|

| Warning | 80% | Alarm — standby DG start command |

| Level 1 Trip | 90% | Non-essential group 1 (accommodation fans, entertainment) |

| Level 2 Trip | 95% | Non-essential group 2 (HVAC, workshop, laundry) |

| Emergency | 100% | All non-essential loads + standby DG start |

#### Manual Restore

After a preferential trip, loads are manually restored by the engineer once:

1. Additional generator capacity is online

2. Bus load has reduced to safe level

3. Fault (if any) is cleared

#### Why Not Auto-Restore?

Auto-restoration of tripped loads could cause re-overload. SOLAS requires that preferential trip loads do not auto-restore without operator action.

### Generator Overload Protection

| Setting | Level | Action |

|---------|-------|--------|

| 80% rated kW | Warning | Audible/visual alarm |

| 90% rated kW | High Alarm | Start standby generator command |

| 100% rated kW | Overload | Trip non-essential loads, alarm |

| 105% rated kW (timed) | Emergency | Generator breaker trip if sustained |

### Load Curve Monitoring

A rolling 60-second load trend allows engineers to:

Anticipate upcoming high demand (e.g., bow thruster start)

Verify load shedding effect

Optimise generator running hours

### Power Factor Considerations

Low PF (<0.8) indicates excessive reactive load — check AVR settings

Generators should share kVAr proportionally

Circulating reactive current = kVAr imbalance between parallel machines

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System