BlueSim Training Guide

Boiler Operation & Control

Engine Room Equipment

Oil-fired auxiliary boiler simulator covering SOLAS II-1/Reg.35 and IACS UR M51 — burner management, water level control, steam raising, and emergency procedures.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Oil-fired auxiliary boiler simulator covering SOLAS II-1/Reg.35 and IACS UR M51 — burner management, water level control, steam raising, and emergency procedures.

## Key Features

Burner Management System (BMS) with pre-purge, ignition, and flame supervision sequence.

Live steam pressure, drum water level, FO temperature, flue gas, and O₂% gauges.

Pipeline lineup valves: main steam stop, feed check, blow-down, FO supply/return.

Alarms: low water level trip, high pressure, flame failure, FO low pressure.

Three scenarios: Cold Start, Low Water Level Emergency, Fuel Oil Changeover.

Auto/manual mode, pressure setpoint control, and bottom blow-down procedure.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| CONTROLS | Displays real-time system data, controls, and status indicators. |
| BOILER P&ID SCHEMATIC | Displays real-time system data, controls, and status indicators. |
| ALARMS & STATUS | Displays real-time system data, controls, and status indicators. |
| VALVE LINEUP | Displays real-time system data, controls, and status indicators. |
| STEAM PRESSURE TREND | Displays real-time system data, controls, and status indicators. |
| STARTUP CHECKLIST | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Boiler Operation & Control — Technical Reference

### Regulatory Framework

#### SOLAS II-1/Regulation 35 — Steam Boilers and Feed Water Systems

Every steam boiler and steam pressure vessel shall be constructed, tested and installed to the satisfaction of the Administration.

All steam boilers shall be fitted with not less than two safety valves of adequate capacity.

Feed water systems shall have at least two independent feed pumps capable of supplying water at the maximum working pressure.

Arrangements shall be made to prevent damage through overheating when the boiler operates with low water.

Low water level alarm and automatic fuel cut-off are mandatory.

#### IACS UR M51 — Oil-Fired Boilers

Applicable to auxiliary and exhaust gas boilers on vessels.

Burner management system (BMS) requirements: pre-purge, ignition sequence, flame supervision, post-purge.

Minimum 15-second pre-purge air flow before ignition.

Flame detector response time: <1 second to trip BMS on flame failure.

Safety valve set pressure: 5% above maximum allowable working pressure (MAWP).

High steam pressure trip: typically set at 103% MAWP.

Low water level trip: 2-level system — WARNING at low level, TRIP at very low level.

#### IACS UR M53 — Boiler Water Treatment

pH: 10.5–11.5 (drum water)

Phosphate: 20–40 ppm

Chloride: <200 ppm

Dissolved oxygen: <0.02 ppm (feed water)

TDS (Total Dissolved Solids): <3500 ppm for high-pressure boilers

---

### Aalborg Auxiliary Boiler — Technical Parameters

#### Typical Auxiliary Boiler Specifications (Aalborg AQ-18 type)

| Parameter | Value |

|-----------|-------|

| MAWP | 7.0 bar (g) |

| Design Pressure | 8.5 bar (g) |

| Normal Operating Pressure | 6.0–6.5 bar (g) |

| Steam Output | 1800 kg/h at 7 bar |

| Heating Surface | 18 m² |

| Fuel Consumption | ~110 kg/h HFO at full load |

| Feed Water Temperature | 60–80°C |

| Drum Water Volume | 1.2 m³ |

| Safety Valve Setting | 7.3 bar (5% above MAWP) |

| Efficiency | 85–88% |

#### Fuel Oil System Parameters

| Parameter | Value |

|-----------|-------|

| FO Temperature (HFO) | 120–135°C (viscosity ~12 cSt) |

| FO Temperature (MGO/MDO) | 20–40°C |

| FO Pressure at Burner | 3.5–4.5 bar |

| FO Viscosity at Burner | 12–15 cSt |

| FO Filter Mesh | 100 μm |

| Low FO Pressure Alarm | <2.5 bar |

| Low FO Pressure Trip | <2.0 bar |

#### Steam System Parameters

| Parameter | Value |

|-----------|-------|

| Normal Steam Pressure | 6.0–7.0 bar (g) |

| Low Steam Pressure Alarm | <4.5 bar |

| High Steam Pressure Alarm | >7.0 bar |

| High Steam Pressure Trip | >7.3 bar |

| Steam Temp (sat. at 7 bar) | 165°C |

#### Water Level Parameters

| Parameter | Drum Level |

|-----------|-----------|

| Normal Operating Range | NWL ±75 mm |

| Low Water Level Warning | NWL −100 mm |

| Low Low Water Level Trip | NWL −150 mm |

| High Water Level Warning | NWL +100 mm |

| Very High Water Level | NWL +150 mm (steam carry-over risk) |

#### Combustion Parameters

| Parameter | Value |

|-----------|-------|

| Excess Air (full load) | 10–15% |

| O₂ in Flue Gas | 2–3% (optimal) |

| CO₂ in Flue Gas | ~12–13% |

| Flue Gas Temperature | 250–320°C |

| High Flue Gas Temp Alarm | >380°C |

| CO Limit | <50 ppm |

---

### Burner Management System (BMS) Sequence

#### Start-Up Sequence

1. Pre-checks: FO temperature, FO pressure, feed water level OK

2. Fan Start: FD fan starts, airflow proven

3. Pre-Purge: 15 seconds minimum at minimum 25% airflow

4. Low Fire Ignition: Pilot burner energised, flame detected within 5 seconds

5. Main Burner: FO solenoid opens, main flame established

6. Flame Supervision: Continuous UV/IR flame detection

7. Modulation: BMS modulates FO/air ratio based on steam pressure

#### Safety Trip Conditions (BMS Auto-Shutdown)

Flame failure (no flame signal > 2 seconds)

High steam pressure (>7.3 bar)

Low low water level

FO low pressure trip (<2.0 bar)

Airflow failure

Manual emergency stop

---

### Pipeline Lineup for Raising Steam (Cold Start)

1. Feed Water System

- Open feed water storage tank outlet valve

- Open feed pump suction valve

- Prime feed pump

- Start feed pump, verify pressure ~8 bar

- Open feed check valve (non-return valve to drum)

- Fill drum to NWL

2. Steam System

- Ensure main steam stop valve CLOSED

- Open boiler vent valve (allows air escape during heating)

- Verify safety valves free — do NOT gag

3. Fuel Oil System

- Confirm HFO in day tank (check level)

- Open FO supply valve from settling/service tank

- Start HFO trace heating, raise to 120°C

- Start FO circulating pump

- Open FO supply to burner

- Open FO return valve

4. Burner Start

- Initiate BMS start sequence

- Observe pre-purge, ignition

- Confirm flame established

- Set burner to low fire

5. Steam Rising

- Monitor drum pressure — raise pressure slowly: ~0.5 bar/15 min

- When pressure reaches 0.5 bar, close vent valve

- Continue raising to 4 bar — test feed check valve

- At working pressure: open main steam stop valve slowly

- Perform blow-down: open blow-down valve for 5–10 seconds, close

6. Handover

- Set to auto pressure control mode

- Set high/low alarm acknowledgement

- Log in engine room log

---

### Blow-Down Procedure

Purpose: Remove dissolved solids, sediment, sludge from drum bottom.

Frequency: at least once per watch (4–8 hours)

Duration: 5–10 seconds per blow-down

Perform at LOW FIRE to minimise water loss

NEVER blow down if drum level is already low

Two-valve system: slow-open valve first, then blow-down valve; close blow-down valve first when finished

TDS check: if >3500 ppm, increase blow-down frequency

---

### Fuel Oil Changeover (HFO to MDO/MGO)

1. Confirm MDO service tank has sufficient level

2. Raise HFO to maximum temperature before changeover

3. Slowly open MDO supply valve while slowly closing HFO supply valve (parallel switchover)

4. Watch FO supply pressure — maintain constant

5. Gradually reduce FO heater temperature as MDO proportion increases

6. Monitor burner flame — MDO burns brighter, bluer flame

7. Switch off trace heating on HFO line if long-term changeover

8. Log changeover with time and tank readings

---

### Interlock Summary

| Interlock | Action |

|-----------|--------|

| Low low water level | BMS trip, feed pump alarm |

| Flame failure | BMS lockout, FO solenoid closed |

| High steam pressure | BMS trip, safety valve lifts |

| FO low pressure | BMS trip |

| Fan airflow loss | BMS trip, pre-purge required before restart |

---

### References

Aalborg Industries: Auxiliary Boiler Operation & Maintenance Manual

IACS UR M51 (2016) — Requirements for Oil-Fired Boilers

SOLAS Chapter II-1, Regulation 35 — Steam Boilers and Feed Water Systems

IMO MSC.1/Circ.1432 — Guidelines for Vessels with Reduced Manning

DNV GL Rules for Classification, Ship, Part 4 Chapter 7 — Boilers

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System