BlueSim Training Guide

Methanol Fuel Gas Supply System Simulator

Fuel Simulators

Methanol FGSS simulator with diesel-to-methanol changeover sequence, vapour detection, invisible flame hazard awareness and ESD response per IGF Code.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Methanol FGSS simulator with diesel-to-methanol changeover sequence, vapour detection, invisible flame hazard awareness and ESD response per IGF Code.

## Key Features

6-step diesel-to-methanol changeover sequence with purge, switchover valve and flow verification.

Methanol vapour monitoring (ppm) with 50 ppm alarm and 100 ppm ESD auto-trip.

Critical safety data panel: flash point 11°C, invisible flame, TLV 200 ppm, material compatibility.

Four training scenarios: fuel changeover, vapour detection, pump failure, emergency reversion.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| FUEL SYSTEM STATUS | Displays real-time system data, controls, and status indicators. |
| METHANOL FUEL SYSTEM SCHEMATIC | Displays real-time system data, controls, and status indicators. |
| MONITORING & ALARMS | Displays real-time system data, controls, and status indicators. |
| PIPELINE STATUS | Displays real-time system data, controls, and status indicators. |
| SUPPLY PRESSURE TREND | Displays real-time system data, controls, and status indicators. |
| OPERATIONS LOG | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

## 4.2 Valve Controls

Click a valve button to toggle its state. Valve states are colour-coded:

Green: OPEN

Red: CLOSED

Amber: TRANSITIONING

Valve Name

STOR TK [O]

DAY INLET [C]

BLOCK 1 [C]

BLOCK 2 [C]

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Methanol Fuel Supply System (FGSS) — Technical Reference

### Regulatory Framework

**IGF Code Part A-1** (as amended by MSC.391(95)): Requirements for methanol and other low-flashpoint liquid fuels.

**IMO MEPC.328(76)**: Adopted guidelines for the development of a ship implementation plan for the consistent implementation of the 0.50% sulphur limit. Methanol qualifies as compliant fuel.

**MARPOL Annex VI**: Air pollution prevention; methanol as zero-sulphur, low-NOx fuel.

**SOLAS II-2/Reg.4**: Fire safety requirements; methanol's low flash point requires enhanced fire protection.

**IMO MSC-MEPC.2/Circ.17**: Interim guidelines for the safety of ships using methanol as fuel.

**Class Rules**: DNV-ST-0083 (Ships using methanol as fuel), LR ShipRight Methanol.

### Methanol Properties — CRITICAL SAFETY DATA

#### Physical Properties

| Property | Value |

|----------|-------|

| Chemical formula | CH₃OH |

| Flash point | **11°C (EXTREMELY FLAMMABLE)** |

| Boiling point | 64.7°C |

| Auto-ignition temperature | 385°C |

| Explosive limits (LEL/UEL) | 6.0% / 36.5% vol in air |

| Density at 15°C | 795 kg/m³ |

| Lower heating value (LHV) | 19.9 MJ/kg |

| Stoichiometric A/F ratio | 6.45 |

#### Health Hazards

**TLV-TWA (ACGIH)**: 200 ppm (exposure limit — skin absorption possible)

**IDLH**: 6,000 ppm

**Toxic to eyes**: can cause blindness; colourless, nearly odourless liquid

**Invisible flame**: methanol burns with an invisible flame (blue/invisible) — EXTREME HAZARD

PPE required: chemical splash goggles, face shield, impervious gloves, chemical suit

#### Compatibility

Attacks some rubbers, plastics; stainless steel, HDPE compatible

NOT compatible with: conventional diesel elastomers, zinc, aluminium alloys

Electrical equipment: EEx (explosion-proof) throughout fuel system zones

### System Overview

#### Fuel Storage

**Main storage tanks**: IMO Type II design (low-pressure, ambient temperature)

**Day tank** (service tank): smaller buffer tank, typically 2–4 hours supply

Location: deck or double-hull, separated from machinery spaces

#### Supply Train

1. Methanol Transfer Pump: transfers from storage to day tank

2. Day Tank: maintains supply buffer; level monitoring critical

3. Methanol Supply Pump: pressurises fuel to engine inlet pressure

4. Flow Meter (Coriolis type): mass flow measurement for fuel consumption

5. Engine Fuel Rail: 6–8 bar, temperature controlled

#### Fuel Changeover Procedure (Diesel → Methanol)

1. Verify methanol in day tank (level > 30%)

2. Start methanol supply pump — confirm pressure

3. Purge fuel line with methanol (drain diesel residue)

4. Actuate switchover valve (3-way valve)

5. Verify methanol flow to engine

6. Monitor NOx, power output, fuel consumption

7. Adjust injection timing (methanol requires different timing)

#### Emergency Methanol → Diesel Reversion

1. Actuate switchover valve to diesel

2. Stop methanol supply pump

3. Close methanol fuel valves

4. Purge methanol from fuel lines

5. Resume normal diesel operation

### Vapour Detection

Electrochemical sensors (0–2000 ppm) in accommodation, engine room, tank holds

Alarm at 50 ppm (MARPOL zone)

ESD at 100 ppm (engine room)

Daily functional checks required

### ESD System

Closes all methanol fuel valves (block valves on day tank outlet, supply pump outlet)

Switches engine to diesel

Activates deluge/water spray if fire detected

Alarms: methanol vapour high, fuel temp high, supply pressure low

### Key Operating Parameters

| Parameter | Normal | Alarm Low | Alarm High |

|-----------|--------|-----------|------------|

| Storage tank level | 20–90% | < 10% | > 95% |

| Day tank level | 30–80% | < 20% | > 90% |

| Supply pressure | 6–8 bar | < 5 bar | > 10 bar |

| Fuel temperature | 20–40°C | — | > 55°C |

| Methanol vapour | < 10 ppm | — | > 50 ppm |

| Flow rate | design ±10% | < 50% design | > 110% design |

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System